## Thermal
ID | Material Description | Thermal Conductivity | Specific Heat | Density | Emissivity | Min Temp for Spread | Flame Spread Parameter | Cone Data File | Heat of Combustion | Comments | Soot Yield | CO2 Yield | H2O Yield | Calibration Factor | Comments2
3 | hardboard, siding | 0.094 | 1170 | 640 | 0.88 | 0 | 0 | null.txt | 0 | ref. Incropera and deWitt, 3rd ed | 0 | 0 | 0 | 1 | ref. Incropera and deWitt, 3rd ed no flame spread data available
4 | hardboard, high density | 0.15 | 1380 | 1010 | 0.88 | 0 | 0 | null.txt | 0 | ref. Incropera and deWitt, 3rd ed, | 0 | 0 | 0 | 1 | ref. Incropera and deWitt, 3rd ed, no flame spread data available
5 | particleboard, low density | 0.078 | 1300 | 590 | 0.88 | 0 | 0 | null.txt | 0 | ref. Incropera and deWitt, 3rd ed | 0 | 0 | 0 | 1 | ref. Incropera and deWitt, 3rd ed. No flame spread data available.
6 | particleboard, high density | 0.17 | 1300 | 1000 | 0.88 | 0 | 0 | null.txt | 0 | ref. Incropera and deWitt, 3rd ed | 0 | 0 | 0 | 1 | ref. Incropera and deWitt, 3rd ed. No flame spread data available.
10 | wood, oak | 0.17 | 2380 | 800 | 0.88 | 0 | 0 | null.txt | 0 |  | 0 | 0 | 0 | 1 | Drysdale Table 2.1, no flame spread data available
11 | brick | 0.69 | 840 | 1600 | 0.88 | 0 | 0 | null.txt | 0 |  | 0 | 0 | 0 | 1 | Drysdale Table 2.1
12 | plasterboard, gypsum paper-faced | 0.16 | 900 | 760 | 0.88 | 380 | 14 | branz1.txt | 3.1 | Material tested by BRANZ 9.5 mm thick | 0.015 | 1.27 | 0.442 | 1 | Material tested by BRANZ 9.5 mm thick
13 | cork | 0.039 | 1800 | 120 | 0.88 | 0 | 0 | null.txt | 0 | no flame spread data available | 0 | 0 | 0 | 1 | no flame spread data available
21 | plasterboard, painted gypsum paper-faced | 0.17 | 900 | 731 | 0.88 | 478 | 3.3 | e1.txt | 4.1 | EUREFIC Material #1 | 0.0034 | 1.27 | 0.442 | 1 | EUREFIC Material #1, lateral spread props from Quintiere, Haynes and Rhodes, J. fpe 7(1) 1995
22 | plywood, ordinary | 0.12 | 2580 | 725 | 0.88 | 164 | 13 | e2.txt | 11.9 | EUREFIC Material #2 | 0.0096 | 1.27 | 0.442 | 1 | EUREFIC Material #2 birch, lateral spread props from Quintiere, Haynes and Rhodes, J. fpe 7(1) 1995
23 | textile wallcovering on gypsum paper-faced plaster | 0.17 | 2875 | 754 | 0.88 | 189 | 7.7 | e3.txt | 7.5 | EUREFIC Material #3 | 0.004 | 1.27 | 0.442 | 1 | EUREFIC Material #3 lateral spread props from Quintiere, Haynes and Rhodes, J. fpe 7(1) 1995
24 | concrete, lightweight | 0.21 | 880 | 800 | 0.5 | 0 | 0 | null.txt | 0 | substrate for EUREFIC ISO 9705 room tests | 0 | 0 | 0 | 1 | substrate for EUREFIC ISO 9705 room tests
25 | concrete | 1.2 | 880 | 2300 | 0.5 | 0 | 0 | null.txt | 0 |  | 0 | 0 | 0 | 1
26 | plywood 4 mm | 0.12 | 1215 | 580 | 0.88 | 164 | 13 | ply104all.txt | 13.2 | CSIRO Plywood 104 - 3 ply Lauan | 0.015 | 1.27 | 0.442 | 1 | CSIRO Plywood 104 - 3 ply Lauan
27 | melamine-faced high density noncombustible board | 0.58 | 900 | 1077 | 0.88 | 527 | 12.7 | e4.txt | 8.5 | EUREFIC material #4 | 0.0088 | 1.27 | 0.442 | 1 | EUREFIC material #4 lateral spread props from Quintiere, Haynes and Rhodes, J. fpe 7(1) 1995
28 | plywood, FR 4 mm | 0.12 | 2850 | 550 | 0.88 | 164 | 13 | pl108all.txt | 12.8 | CSIRO - three ply hoop pine, FIREX impregnated | 0.015 | 1.27 | 0.442 | 1 | CSIRO - three ply hoop pine, FIREX impregnated
29 | polystyrene, FR | 0.03 | 1000 | 37 | 0.88 | 354 | 11.5 | e11.txt | 27 | EUREFIC material #11 | 0.135 | 2.3 | 1.636 | 1 | EUREFIC material #11, lateral spread props from Quintiere, Haynes and Rhodes, J. fpe 7(1) 1995
32 | polyurethane foam covered with plastic/steel sheet | 0.03 | 1000 | 158 | 0.22 | 326 | 22 | e9.txt | 6.5 | EUREFIC Material #9 | 0.13 | 1.55 | 1.636 | 1 | EUREFIC Material #9 plastic faced steel, lateral spread props from Quintiere, Haynes and Rhodes, J. fpe 7(1) 1995
34 | plastic faced steel sheet on mineral wool | 0.22 | 1000 | 1077 | 0.88 | 472 | 44 | e5.txt | 11 | EUREFIC material #5 | 0.055 | 1.27 | 0.442 | 1 | EUREFIC material #5 lateral spread props from Quintiere, Haynes and Rhodes, J. fpe 7(1) 1995
35 | pvc carpet on gypsum paper plasterboard | 0.17 | 1810 | 815 | 0.88 | 367 | 8.2 | e10.txt | 6.5 | EUREFIC material #10 | 0.015 | 0.46 | 0.442 | 1 | EUREFIC material #10 lateral spread props from Quintiere, Haynes and Rhodes, J. fpe 7(1) 1995
36 | particleboard, FR | 0.08 | 1300 | 630 | 0.88 | 482 | 8 | e6.txt | 3.9 | EUREFIC material #6 | 0.012 | 1.27 | 0.442 | 1 | EUREFIC material #6 lateral spread props from Quintiere, Haynes and Rhodes, J. fpe 7(1) 1995
37 | cellulose insulating fibreboard (FR coated) | 0.055 | 1300 | 300 | 0.88 | 90 | 14 | branz3.txt | 9.4 | BRANZ material # 3 | 0.015 | 1.27 | 0.442 | 1 | BRANZ material # 3, ceiling tile
38 | ceramic fibre insulation board | 0.09 | 1040 | 128 | 0.97 | 0 | 0 | null.txt | 0 | steckler tests | 0 | 0 | 0 | 1 | steckler tests k=0.09 at 300C k=0.17 at 600C k=0.25 at 900C
39 | plasterboard | 0.16 | 900 | 810 | 0.88 | 0 | 0 | null.txt | 0 | noncombustible | 0 | 0 | 0 | 1 | inert
40 | cellulose insulating fibreboard | 0.06 | 1300 | 350 | 0.88 | 90 | 14 | ifb.txt | 12.3 | tested by BRANZ, non FR | 0.015 | 1.27 | 0.442 | 1 | tested by BRANZ, non FR
62 | polyurethane foam, rigid, simulated | 0.02 | 1300 | 118 | 0.88 | 105 | 3 | quint_s11.txt | 13 | Quintiere FSJ 20 (1993) cone hrr estimated | 0.13 | 1.5 | 1.6 | 1 | Quintiere FSJ 20 (1993) cone hrr estimated
63 | plywood, rough sawn | 0.12 | 1215 | 583 | 0.88 | 120 | 12.9 | rsply.txt | 12.1 | BRANZ tested material, H3 LOSP clear, bandsawn | 0.015 | 1.27 | 0.442 | 1 | BRANZ tested material, H3 LOSP clear, bandsawn
64 | fibre cement sheet | 0.72 | 840 | 1490 | 0.88 | 100 | 3 | fcs.txt | 3.42 |  | 0 | 0 | 0 | 1 | Hardiflex
65 | pvc, foamed | 0.03 | 1810 | 70 | 0.9 | 100 | 10 | pvc.txt | 8.4 |  | 0.172 | 0.46 | 0.442 | 1 | weatherboard
66 | steel (mild) | 45.8 | 460 | 7850 | 0.9 | 0 | 0 | null.txt | 0 |  | 0 | 0 | 0 | 1 | Drysdale Table 2.1
67 | glass (plate) | 0.76 | 840 | 2700 | 0.9 | 0 | 0 | null.txt | 0 |  | 0 | 0 | 0 | 1 | Drysdale Table 2.1
68 | wood, yellow pine | 0.14 | 2850 | 640 | 0.88 | 0 | 0 | null.txt | 0 |  | 0 | 0 | 0 | 1 | Drysdale Table 2.1. No flame spread data available.
70 | fire brick | 0.36 | 1040 | 750 | 0.8 | 0 | 0 | null.txt | 0 |  | 0 | 0 | 0 | 1 | NBSIR 88-3752 k=0.36 at 200C k=0.38 at 300C k=0.45 at 600C
71 | calcium silicate | 0.12 | 1250 | 720 | 0.83 | 0 | 0 | null.txt | 0 |  | 0 | 0 | 0 | 1 | at 200C
72 | plasterboard (Australia) | 0.16 | 900 | 810 | 0.88 | 380 | 14 | pb115all.txt | 3.1 |  | 0.015 | 1.27 | 0.442 | 1 | CSIRO Material PB115
74 | Timber, unvarnished spruce | 0.12 | 2580 | 450 | 0.88 | 164 | 13 | m12.txt | 12 |  | 0.015 | 1.27 | 0.442 | 1 | from SBI research
75 | medium density fibreboard | 0.12 | 2580 | 700 | 0.88 | 160 | 13 | m25.txt | 12 |  | 0.015 | 1.27 | 0.442 | 1 | SBI research
76 | wood | 0.117 | 1630 | 400 | 0.88 | 0 | 0 | null.txt | 12 |  | 0 | 0 | 0 | 1 | JET test
78 | Kaowool HT ceramic fibre board | 0.068 | 1090 | 336 | 0.9 | 0 | 0 | null.txt | 0 |  | 0 | 0 | 0 | 1 | k @ 260C = 0.068 k @ 538C = 0.098
79 | polystyrene, FR extruded, 40 mm | 0.03 | 1000 | 32 | 0.9 | 354 | 11.5 | M03.txt | 27 |  | 0.162 | 2.3 | 1.636 | 1 | SBI Research Material M03
80 | timber, varnished pine, 10 mm | 0.12 | 2850 | 380 | 0.88 | 164 | 13 | M05.txt | 13 |  | 0.015 | 1.27 | 0.442 | 1 | SBI Material M05
81 | Polycarbonate, FR 3 layers, 16 mm | 0.03 | 1000 | 175 | 0.88 | 0 | 0 | M07.txt | 20.6 |  | 0.091 | 1.65 | 1.6 | 1 | SBI Material M07 yields guessed using polyester data from Tewarson (1995)
88 | ceramic fibreboard | 0.08 | 1090 | 336 | 0.9 | 0 | 0 | null.txt | 0 |  | 0 | 0 | 0 | 1
90 | ply, untreated aged 9mm | 0.12 | 1215 | 445 | 0.88 | 120 | 13 | agedply.txt | 10.1 |  | 0.015 | 1.27 | 0.442 | 1 | PNW
91 | Tukutuku Panel | 0.12 | 2850 | 400 | 0.88 | 160 | 13 | tukutuku.txt | 10.8 |  | 0.015 | 1.27 | 0.44 | 1 | A composite panel of thin tmber slats, woven with flax over toitoi reeds. Used in traditional NZ marae. Thermal props assumed as for timber, except HoC.
92 | Plywood 7 mm | 0.12 | 1215 | 523 | 0.88 | 170 | 7.4 | 7mmPlyUC.txt | 13.3 |  | 0.015 | 1.27 | 0.442 |  | as used by H Peel. see Interflam 2016
93 | CLT | 0.13 | 1600 | 515 | 1 | 0 | 0 | null.txt | 14 |  | 0.015 | 1.27 | 0.442
94 | Gypsum Board, Type X (5/8 in) | 0.14 | 900 | 770 | 0.9 | 0 | 0 | null.txt | 0 |  | 0 | 0 | 0 |  | CFAST value
95 | Fiber Cement 25.4mm + Gyps X5/8 31.8mm | 0.4 | 864 | 1090 | 0.88
96 | FCiment 25.4 + GypsX 31.8+Concrete 150mm | 0.98 | 877 | 1966 | 0.88
97 | Plywood 7mm + FCiment 25.4mm_CFAST | 0.59 | 873 | 1281 | 0.88 | 0 | 0 | null.txt | 0 |  | 0 | 0 | 0 |  | Withour cone file
98 | KAOWOOL | 0.22 | 1047 | 128 | 0.97 | 0 | 0 | null.txt | 0 |  | 0 | 0 | 0 |  | Cfast Mineral Fiber Insulation (1/2 in)
99 | GlassFibre 1 | 0.04 | 720 | 105 | 0.9 | 0 | 0 | null.txt | 0 |  | 0 | 0 | 0 |  | CFast GLASFIBR
100 | GYP1/2 | 0.16 | 900 | 790 | 0.9 | 0 | 0 | null.txt | 0 |  | 0 | 0 | 0 |  | CFast Gypsum Board (1/2 in)
101 | HARDWOOD | 0.16 | 1255 | 720 | 0.9 | 0 | 0 | null.txt | 0 |  | 0 | 0 | 0 |  | CFast Hardwood (oak, maple) (3/4 in)
102 | plasterBoard Type F | 0.24 | 950 | 784 | 0.9 | 0 | 0 | null.txt | 0 |  | 0 | 0 | 0 |  | Hadden et al in Effects of exposed cross laminated timber on compartment fire dynamics
103 | Stone wool insulation | 0.039 | 700 | 164 | 0.9 | 0 | 0 | null.txt | 0 |  | 0 | 0 | 0 |  | Hadden et al in Effects of exposed cross laminated timber on compartment fire dynamics
104 | Aerated concrete blocks | 0.36 | 1000 | 350 | 0.5 | 0 | 0 | null.txt | 0 |  | 0 | 0 | 0 |  | Epernon Table 5
105 | Calcium silicate board | 0.212 | 1000 | 900 | 0.88 | 0 | 0 | null.txt | 0 |  | 0 | 0 | 0 |  | Epernon Table 5
106 | Mineral wool | 0.05 | 1000 | 96 | 0.9 | 0 | 0 | null.txt | 0 |  | 0 | 0 | 0 |  | Epernon Table 5
107 | CLT (epernon) | 0.12 | 1530 | 450 | 1 | 0 | 0 | null.txt | 0 |  | 0 | 0 | 0 |  | Epernon Table 5
108 | Concrete (epernon) | 1.33 | 900 | 2400 | 0.5 | 0 | 0 | null.txt | 0 |  | 0 | 0 | 0 |  | Epernon Table 5